## Intro
Existing Building Commissioning (EBCx) is an optimization process for existing buildings that includes the terms recommissioning (RCx), retro-commissioning (Re-Cx) and ongoing commissioning (OCx). EBCx helps ensure that systems are operating optimally to meet occupants needs and provides a rigorous investigation to identify performance and integration issues. A primary focus of EBCx is to deliver “low-cost/no-cost” operational improvements to maximize comfort and energy savings. EBCx can be carried out as a standalone process or done in concert with a retroﬁt project. This EBCx Pre-Screening Tool has been developed to help select the best building candidate(s) for existing building commissioning. Prioritizing a portfolio of buildings and selecting those that are the most ready and have the greatest potential for improvement can assist with long-term planning and enable building owners to take advantage of short term paybacks. This tool is designed to be used at the planning phase of the standardized EBCx process. A score for each building is provided, representing the readiness for EBCx at the current point in time. Refer to the User Guide tab, question mark icons throughout the tool, or the link below for insights and additional information on how to complete this screening tool.
Link to NRCan's guide, case studies and tools on EBCx:
natural-resources.canada.ca/existing-building-commissioning
| ACKNOWLEDGEMENTS Natural Resources Canada would like to thank the following organizations for their assistance during the development of the tool: Prism Engineering and Portland Energy Conservation Inc. (PECI). As part of the various consultations conducted, numerous other organizations provided comments and suggestions for improvements. Their efforts are also gratefully acknowledged. REPRODUCTION This tool and accompanying data are copyright of the Minister of Natural Resources Canada (2025). Duplication in any manner is forbidden without prior written permission, which may be obtained by contacting CanmetENERGY. © Minister of Natural Resources Canada 2025. | DISCLAIMER & INDEMNIFICATION This tool is provided on an “as is” basis. Natural Resources Canada nor does its minister, officers, employees or agents make any representations or warranties, either expressed or implied, arising by law or otherwise, including but not limited to, implied warranties of merchantability or fitness for a particular purpose, or that the use of this tool will not infringe any intellectual property rights of third parties. In no event will Natural Resources Canada nor its minister, officers, employees or agents have any obligations or liability arising from tort, or for loss of revenue or profit, or for indirect, special, incidental or consequential damages as a result of your use of this tool. This tool is distributed for informational purposes only and does not necessarily reflect the views of the Government of Canada nor constitute an endorsement of any commercial product or person. Neither Canada, nor its ministers, officers, employees and agents make any warranty in respect to this tool nor assume any liability arising out of this tool. The recipient of this tool shall indemnify and save harmless Natural Resources Canada, and its employees and agents, from and against, and shall be responsible for all claims, demands, losses, costs, including solicitor and client costs, damages, action suits or proceedings, arising out of, related to, or occasioned by any use of this tool by the recipient. Natural Resources Canada shall have the right to defend any such action or proceeding with counsel of its own selection.
NRCan/CanmetENERGY v5.7
(EBCx) PRE-SCREENING TOOL

## User Guide
EBCx Pre-Screening Tool USER GUIDE
Use this tool by entering information and answering questions on your buildings from various drop down menus. Although drop downs have the option to enter 'Unsure' for most questions, the more information you provide the tool, the more accurate and meaningful the results in the Report will be.
Start in the 'Facilty' tab - this tab includes questions about the buildings in your porfolio.
Next enter information in the 'Energy' tab - this tab includes questions about the energy use of your buildings.
Finally an automated report is generated in the 'Report' tab. This report provides insights into the EBCx Readiness Score for each building.
Any time you see this symbol you can single click the icon to gain more information on the specific question being asked.
Macros and ActiveX Controls – Security Notice This Excel tool includes approved Microsoft macros and ActiveX controls required for its automated functions. When opening the file for the first time, Microsoft Excel may display a Security Warning indicating that macros and/or ActiveX controls have been disabled or blocked. To ensure full functionality of this tool, users must allow both macros and ActiveX content. To enable the required content, please click on the warning icon that appears in Excel and follow the official Microsoft guidance. You can also click on the following links:
Enable or disable macros in Microsoft 365 files
Enable or disable ActiveX settings in Office files - Microsoft Support

## Facility
Hide |  | Show stopper controls type | Pneumatic control
Hide |  | Show stopper floor area | 2000 | m2 or less | [14 empty] | Hide >>
Hide
Hide
Hide
Hide
Hide
EBCx Pre-Screening Tool FACILITY INPUTS PAGE
Rationale to question/Notes - to be hidden from user
| How many buildings would you like to assess for EBCx readiness? |  | 16
Depending on number entered, table will open up with x number of columns, one per building
Building
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
SITE INFORMATION
1 | Enter the Building Name (required)
2 | Building Location (Province) (required) | [17 empty] | Used to prepopulate default GHG emission intensity factor for electricity, to estimate site emissions.
3 | Building Type (required)
4 | Approximate floor area of conditioned space (square meters - m2) (required)
SYSTEMS
5 | What is the primary type of building control system you have in this building? | bar: Building 3 to Building 15
6 | If you have a digital building controls system does it have remote (off-site) access that is available for an external consultant to use? | bar: Building 3 to Building 15
7 | Does the digital building controls system have capabilities to log and trend data? | bar: Building 3 to Building 15
8 | Are you proceeding with a major redesign or replacement of your HVAC or control systems in the building in the near future? | [17 empty] | If a major redesign will occur, the persistence of measures is likely to be low. This also includes significant replacement of equipment at end of life. It is advisable to wait until after the redesign/upgrade to commence EBCx. | bar: Building 3 to Building 15
9 | How often do you experience premature failure of building equipment, control systems, or both in this building? | bar: Building 3 to Building 15
10 | Are there concerns that water consumption for this building is higher than expected? | bar: Building 3 to Building 15
11 | Are there known opportunities related to the building envelope that could improve energy performance? | bar: Building 3 to Building 15
OPERATION
12 | Is the primary space use of the building expected to significantly change in the next 5 years? | [17 empty] | If No, priority goes down | bar: Building 8
13 | How often are thermal comfort or indoor air quality (IAQ) complaints received from building occupants/tenants? | bar: Building 8
14 | Has the building been through a comprehensive recommissioning process where measures were implemented within the past 5 yrs? | [17 empty] | If Yes, priority goes down | bar: Building 8
15 | Does the building currently have an Energy Performance Contract (EPC) in place? | bar: Building 8
ORGANIZATION
16 | Does the organization have the financial resources to implement low cost measures identified during the EBCx process at this building? | bar: Building 8
17 | How engaged are your operators and staff with respect to building optimization? | bar: Building 8
18 | Do you have access to mechanical drawings for the building? | bar: Building 8
19 | Do you have access to balancing reports for the building? | bar: Building 8
20 | What is the primary motivating factor of the organization in terms of performance improvements (for all buildings)? | [17 empty] | Used to provide weighting to either GHG, Energy, or Cost for building
ENERGY AND EMISSIONS PERFORMANCE
| Has the building energy use recently been trending upward without a known cause? |  | Building 1: Yes; Building 2: No |  | Yes' indicates greater potential for RCx
| Do you track this building's energy performance in Energy Star Portfolio Manager (ESPM)? | [17 empty] | Note: Tough to benchmark if some building use ESPM score and some use raw data. Suggest we ask upfront if they wish to review the performance of ALL their building using one or the other, and then that has to be used for ALL buildings they enter. | bar: Building 1 to Building 2
| If yes, enter your ESPM score here | [17 empty] | Hide row if not needed. If ESPM score used, hide all other energy data input rows.
| If no, then enter your energy information in the rows below | [17 empty] | Hide row if not needed
| Annual electricity consumption (kWh/year) |  | Building 1: 200000; Building 2: 500000 | Approximate is ok. | Used to calculate EUI. Nominal consumption also used in eval.
| Annual fuel consumption (GJ/yr) |  | Building 1: 350; Building 2: 50 | Approximate is ok.
| Fuel type |  | Building 1: Natural Gas; Building 2: Propane |  | Used to calculate GHG emissions from fuel. GHG data used to help prioritize.
| Annual energy cost ($/yr) |  | Building 1: 24900; Building 2: 50700 | Approximate is ok. | Buildings with higher energy cost rank higher
| Annual Energy Use Intensity - EUI (ekWh/m2) |  | Building 1: #DIV/0!; Building 2: #DIV/0! | This is the combined electricity and fuel consumption per m2, per year | EUI is good but will work best for office and schools. Other facility will be hard to evaluate, e.g pools, community centres, hospitals, large retail. These sites could be an automatic yes….
| Do you know or have access to the GHG emissions data for this building? |  | Building 1: Yes; Building 2: No |  | If yes, then let user populate. If not, use default GHG intensities to estimate.
| If yes to previous question, enter the annual GHG emissions for this building | [16 empty] | Approximate is ok. | Hidden if user does not have own GHG data
| (If no) Estimated Annual GHG emissions (tons CO2e/yr) |  | Building 1: 23.353; Building 2: 3.079 |  | Hidden if user enters own GHG data
| Annual GHG intensity - GHGi - (kg CO2e/m2) |  | Building 1: #DIV/0!; Building 2: #DIV/0!
Note on D1: Sam Thomas: Do not delete or alter text
Note on D2: Sam Thomas: Do not delete or alter.
Note on B52: Sam Thomas: Could ask for ESPM score instead, or let them choose if they want to use ESPM score or just raw data.
Note on C52: Sam Thomas: Could ask for ESPM score instead, or let them choose if they want to use ESPM score or just raw data.
Note on B62: Sam Thomas: Could ask question if GHG is a focus or not first, and don't ask any of this if it's not.

## Energy
Manual entry or RETScreen
Energy Star Portfolio Manager | 0 | 16 |  | EBCx Pre-Screening Tool ENERGY DATA INPUT PAGE
0
Manual entry or RETScreen
1 = show
Show/Hide row |  | Show/Hide row
FILTER
1 | 1 | 1
1 | 1 | 1 |  | How would you like to enter energy data for your buildings into this tool?
0 | 1 | 0 |  | Number of buildings included | HIDDEN | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
1 | 1 | 1
1 | 1 | 1 |  | ENERGY AND EMISSIONS PERFORMANCE
0 | 1 | 0 |  | Building | HIDDEN | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
1 | 1 | 1 |  | Building Name
1 | 1 | 1 |  | Building Type
0 | 1 | 0 |  | Province | HIDDEN
1 | 1 | 1 |  | Floor area (m2)
0 | 0 | 0 |  | ESPM rows | HIDDEN
1 | 1 | 1
0 | 1 | 0 | 1 | ENERGY STAR Score for the building (0 to 100)
0 | 0 | 0 | 2 | Annual Energy Cost for the building |  | 0 | 0 | 0 | 0
0 | 0 | 0 | 3 | Total GHG Emissions Intensity for the building (kgCO2e/m2)
0 | 1 | 0
0 | 1 | 0 |  | Raw data / RETScreen rows | HIDDEN
1 | 1 | 1 | 1 | Annual electricity consumption (kWh/year) - ELECTRICITY
1 | 1 | 1 | 2 | Select Primary Fuel Type - FUEL 1
1 | 1 | 1 | 3 | Annual fuel consumption (GJ/yr) - FUEL 1
1 | 1 | 1 | 4 | Select Secondary Fuel Type - FUEL 2
1 | 1 | 1 | 5 | Annual fuel consumption (GJ/yr) - FUEL 2
1 | 0 | 0 | 6 | Annual energy cost ($/yr) (Total of all energy types)
1 | 1 | 1 | 7 | Annual Energy Use Intensity - EUI (ekWh/m2)
0 | 1 | 0 |  | FUEL 1 - Fuel emissions factor (tons/GJ) | HIDDEN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1 | 0 |  | FUEL 2 - Fuel emissions factor (tons/GJ) | HIDDEN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 0 | 0 | 8 | Default electricity emission factor (tons/kWh)
1 | 0 | 0 | 9 | Optional user entered electricity emission factor (tons/kWh)
0 | 1 | 0 |  | Elec factor to use | HIDDEN
0 | 1 | 0
1 | 0 | 0 | 10 | Estimated Annual GHG emissions (tons CO2e/yr)
1 | 0 | 0 | 11 | Annual GHG intensity - GHGi - (kg CO2e/m2)
1 | 1 | 1
0 | 1 | 0 |  | General - show regardless of data entry method | HIDDEN
1 | 1 | 1 | 12 | Has energy use been trending upward without known cause?
Note that weather normalization of energy data and a review of climate impact are not included as part of this tool.
Note on D1: Sam Thomas: This cell must be unprotected (not locked)
Note on E1: Sam Thomas: This cell must be unprotected (not locked)
Note on D2: Sam Thomas: This cell must be unprotected (not locked)
Note on E2: Sam Thomas: This cell must be unprotected (not locked)
Note on D3: Sam Thomas: This cell must be unprotected (not locked)
Note on E3: Sam Thomas: This cell must be unprotected (not locked)
Note on D4: Sam Thomas: This cell must be unprotected (not locked)
Note on E4: Sam Thomas: This cell must be unprotected (not locked)
Note on F6: Sam Thomas: If a row = 1, that row will be shown to the user.
Note on E21: Sam Thomas: =1 if 'Cost reduction' is org priority
Note on E22: Sam Thomas: =1 if 'GHG emissions' are org priority
Note on E30: Sam Thomas: =1 if 'Cost reduction' is org priority
Note on E34: Sam Thomas: =1 if 'GHG emissions' are org priority
Note on E35: Sam Thomas: =1 if 'GHG emissions' are org priority
Note on E38: Sam Thomas: =1 if 'GHG emissions' are org priority
Note on E39: Sam Thomas: =1 if 'GHG emissions' are org priority

## Report
EBCx PRE-SCREENING TOOL REPORT
INTRODUCTION:
This report outlines the results of a pre-screening assessment used to aid in the planning for Existing Building Commissioning (EBCx). The results outline the EBCx Readiness Score and recommended next steps on a building by building basis. The information provided by this tool is based on user defined inputs, is intended to be preliminary only, and accuracy is not guaranteed. Scores represent where each building ranks now, at this point in time. It is important to reassess buildings again in the future (at least every 5 years) as scores will change over time.
RESULTS:
The table below summarizes the buildings assessed in this tool and their respective EBCx Readiness Score. A score of 10 represents an ideal candidate for EBCx, and a score of 0 a poor candidate. The scores are relative to other buildings in the portfolio entered into the tool.
[6 empty] | 10: Ideal Candidate | 0: Poor Candidate
Building number | Building Name | EBCx Readiness Score | Recommendation | Show/Hide | Building Name | EBCx Readiness Score | Recommendation
5 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
6 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
7 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
8 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
9 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
10 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
11 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
12 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
13 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
14 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
15 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
2 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
4 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
3 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
1 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
RESOURCES:
To proceed with EBCx for viable buildings, the guide developed by NRCan provides detailed information about the recommissioning process from planning through to completion, and outlines best practices to follow. The guide, along with additional resources and tools, can be found here:
natural-resources.canada.ca/existing-building-commissioning
The CSA Z5001 Standard provides guidelines for the commissioning of systems for building energy use through the building envelope, mechanical and electrical equipment, and water uses. Find out more here:
https://www.csagroup.org/store/product/CSA%20Z5001:20/
COMMENTS:
Use the free-form box below to enter any comments or next steps to help you move forward with EBCx on your buildings:
Prepared by:
Date:

## -------- (hidden)
Intentionally blank

## Lookup tables (hidden)
THIS TAB USED FOR ENERGY & EMISSION LOOKUPS
HIDE TAB FROM USER
| GHG Intensity - Electricity |  | Default GHG intensity factor
Electricity
| Province |  | g CO2e/kWh | T CO2e/kWh | Year | Source
| AB | Alberta | 620 | 0.00062 | 2020 | Greening Govt
| BC | British Columbia | 11.3 | 1.13e-05 | 2023 | BC Integrated Grid
| MB | Manitoba | 1.2 | 1.2e-06 | 2020 | Greening Govt
| NB | New Brunswick | 260 | 0.00026 | 2020 | Greening Govt
| NL | Newfoundland & Labrador | 27 | 2.7e-05 | 2020 | Greening Govt
| NS | Nova Scotia | 710 | 0.00071 | 2020 | Greening Govt
| NT | Northwest Territories | 200 | 0.0002 | 2020 | Greening Govt
| NU | Nunavut | 850 | 0.00085 | 2020 | Greening Govt
| ON | Ontario | 30 | 3e-05 | 2020 | Greening Govt
| PE | Prince Edward Island | 260 | 0.00026 | 2020 | Greening Govt
| QC | Quebec | 1.2 | 1.2e-06 | 2020 | Greening Govt
| SK | Saskatchewan | 660 | 0.00066 | 2020 | Greening Govt
| YT | Yukon | 101 | 0.000101 | 2020 | Greening Govt
GHG Intensity - fuels
|  |  | kg/GJ | T CO2e/GJ
|  | Natural Gas | 49.58 | 0.04958
|  | Propane | 61.15 | 0.06115
|  | Light fuel oil | 68.37 | 0.06837
|  | Biomass | 2.24 | 0.00224
|  | RNG (100%) | 0.2932 | 0.0002932
|  | RNG (66%) | 17.0507 | 0.017051
|  | RNG (33%) | 33.3154 | 0.033315
|  | None | 0 | 0
Note on G7: Sam Thomas: https://www2.gov.bc.ca/gov/content/environment/climate-change/industry/reporting/quantify/electricity

## DropDowns (hidden)
THIS TAB USED TO PROVIDE TEXT FOR DROP DOWN MENUS USED THROUGHOUT TOOL. Text can be edited as required, but do not move cells or add rows/columns
HIDE FROM USER | Province |  | Building Type | General 1 | Complaints | Organizational focus | Controls type | Frequency | Energy Data Input | Engagement
| AB | Alberta | Banking/Financial | Yes | Never | GHG reduction | Direct Digital Control (DDC) | Annually | Manual entry or RETScreen | High engagement
| BC | British Columbia | Data Center | No | Infrequent | Energy reduction | Pneumatic control | Seasonally | Energy Star Portfolio Manager | Some engagement
| MB | Manitoba | Education - K-12 | Unsure | Regularly | Cost reduction | Combination DDC & Pneumatic | Monthly |  | Low engagement
| NB | New Brunswick | Education - Other |  | Constant | Comfort & Operation | Web based smart thermostats | Weekly |  | No engagement
| NL | Newfoundland & Labrador | Education - Post Secondary |  | Unsure | Other | Local programmable thermostats | Daily |  | Unsure
| NS | Nova Scotia | Entertainment |  |  | Unsure | Manual control | Unsure
| NT | Northwest Territories | Food - Other | General 2 |  |  | Other
| NU | Nunavut | Food - Restaurant & Bar | Yes |  |  | Unsure
| ON | Ontario | Food - Supermarket | No
| PE | Prince Edward Island | Health - Hospital | Not applicable
| QC | Quebec | Health - Other | Unsure
| SK | Saskatchewan | Industrial - Other
| YT | Yukon | Laboratory
Lodging - Hotel
Lodging - Other
Manufacturing
Office
Office/Retail Mixed
Public - Emergency Services
Public - Library
Public - Water/Waste
Public - Recreation
Religious Worship
Residential Multi Unit
Retail
Retail - Mall
Retail - Other
Retail - Store
Warehouse
OTHER
Note on E2: Sam Thomas: Intent is to align with ESPM building types https://www.energystar.gov/buildings/benchmark/understand_metrics/property_types
Note that the same building types are used in the EUI tab. Do not change naming here without also changing in EUI tab

## Help icons (hidden)
THIS TAB PROVIDES TEXT USED IN HELP ICONS. DO NOT ADD ROWS/COLUMNS OR REARRANGE CELLS. VBA CODE REFERENCES EXACT CELLS FROM THIS TAB. TEXT CAN BE MODIFIED THOUGH.
HIDE FROM USER | Tab | Question (abbreviated) | Help icon response text (TEXT CAN BE MODIFIED BELOW AS REQUIRED)
| FACILITY | Building Type | Select the most appropriate building type from the drop down that represents the majority of space usage in the facility. If option not shown, select 'Other'.
| FACILITY | Floor area | Conditioned space refers to the area of the building for which HVAC is provided. Parkades are usually excluded. Be sure to enter values in square meters (m2).
| FACILITY | Control type | Select the controls type that best represents the type used for the majority of your HVAC systems.
| FACILITY | Major redesign | A major redesign or replacement is a change that would impact more than roughly one third of your HVAC systems.
| FACILITY | Water consumption | High water consumption can also be a good indicator of the need for EBCx (with an added focus on water usage).
| FACILITY | Building envelope | Known opportunities could include windows and doors in poor condition, degraded insulation, water ingress, or severe drafts.
| FACILITY | RCx in past 5 yrs | A comprehensive recommissioning process would include an investigation, findings report, implementation of measures, and checking to ensure measures persist. This is often supported by an external consultant. According to best practices, the RCx process should be repeated every 5 years (appx) to maximize and maintain its benefits over time.
| FACILITY | Energy Perf Contract | An Energy Performance Contract (EPC) is a performance-based financing mechanism that enables a client organization to leverage the technical and financial capacity of an Energy Service Company (ESCO) to design, build, and secure financing to improve energy management practices and/or retrofits within a facility. Having an active EPC in place may impact the ability to make additional changes as part of an EBCx process, requiring careful coordination with the EPC provider. If you already have an EPC in place, consider the impacts of the Energy Performance Contract (EPC) on the ability to implement energy improvements. One of the ways to consider these impacts is to establish a new energy performance baseline after the implementation of the EPC measures. If an EPC is planned for in the next 5 years, it is recommended to wait until the EPC measures have been implemented before considering EBCx for this building.
| FACILITY | Financial resources | Although EBCx typically identifies low cost / no cost opportunities, some funding will still be required to undertake an investigation and implement the results. A total budget of $0.30 - $0.50 / ft2 is advisable to carry for the entire EBCx process. In some cases this may be offset by program funding/incentives.
| FACILITY | Motivating factor | This applies to the organization as a whole, not just for one building. If multiple factors apply, choose the one that holds the largest weight within the organization.
| FACILITY | Number of buildings | Select up to 15 buildings you would like to compare by using the up/down arrows.
| FACILITY | DDC trending capability | Ideally the control system would be able to log and trend data for at least 2 weeks at an interval of 15 minutes. This data is particularly useful for investigation of opportunities, and verifying implementation.
| FACILITY | Engagement | Having engagement from operators and staff is a large part of a successful EBCx project. If your operators are not currently engaged, it is recommended that this is a focus prior in the initial stages of the EBCx process.
| FACILITY | Space use changes | Proposed space use changes may have an impact on the effectiveness of the EBCx process. As according to best practices, the recommissioning process should be repeated every 5 years (appx) to maximize and maintain its benefits over time. If significant space use changes are planned in the next 5 years, you may wish to wait to proceed with an EBCx after these modifications are complete.
FACILITY
| FACILITY | (space left for additional help icons if needed)
| FACILITY | WARNING - Building is smaller than threshold in cell below | This building floor area is small and the return on investment for EBCx may be low when compared to other larger buildings. Consider a light version of EBCx for this building, focusing only on primary energy consuming equipment. The EBCx Readiness Score shown in the Report is likely to be low for this building due to it's size. However there may still be opportunity for energy performance improvement. Click OK to continue.
| FACILITY | Too small size less than threshold (m2) | 2000 | 21527.8 | ft2
| FACILITY | WARNING - Pneumatic controls | This building is a poor candidate for EBCx due to the limited optimization available with pneumatic controls. It is recommended to prioritize the upgrade to a modern control system before proceeding with EBCx. You can continue to enter information on this building, however the EBCx Readiness Score will be low. Click OK to continue.
| ENERGY | Energy use trend upwards | If energy use and/or costs have been increasing significantly and the reason cannot be explained, select 'Yes'. Reasons for increasing energy might include higher occupant density, renovations, longer operating hours, increased ventilation requirements, etc.
| ENERGY | Energy Data Inputs | Enter the most recent full year of consumption data you have available. If you do not have data, leave these cells blank. Up to two fuel types can be entered. If only one fuel type is used, leave the second fuel type blank, or select 'None'. If you do not use fuel, leave fuel cells blank.
| ENERGY | Elec Emission Factors | A default electricity emission factor is provided based on Provincial averages published by Canada. If you wish to override this default factor and enter your own, you can do so here and the default value will be ignored. If you wish to use the default value, leave the User Entered cell blank.
| ENERGY | ESPM | Energy Star Portfolio Manager (ESPM) is an interactive online tool that enables you to benchmark the energy use of any type of building. Buildings receive a 1 – 100 ENERGY STAR score, which compares your building to similar buildings nationwide. A score of 50 represents median energy performance, while a score of 75 or higher means your building is a top energy performer. For more information visit: www.energystar.gov/buildings/benchmark
Note on D2: Sam Thomas: Text here not referenced in help icons
Note on D20: Sam Thomas: This value is referenced by VBA code and can be adjusted if required.

## Scoring (hidden)
THIS TAB DETERMINES EBCX SCORE FOR EACH BUILDING AND ASSOCIATED TEXT USED IN REPORT |  |  | Question>> | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  |  | 20
Notes | If the user answers 'unsure' for any question, the score for that question is ignored. |  | Score | Floor area m2 | Primary building use change | IAQ | RCx past 5yrs | EPC in place | Financial resources | Mech dwgs | Balance. Rpts. | Cntrl system type | DDC remote access | DDC trend logs | Major redesign planned | Premature failure of equip. | Water consumption high | Envelope issues | Energy trending upwards | Energy cost | EUI | GHGi | Engagement | (spare) | Score | Controls type | Score
| Cells in orange can be changed by the tool owner (not the user) |  | 0 | 1: 0; 10: (table to right) |  |  | 0 | Direct Digital Control (DDC) | 5
| Do NOT add rows, columns, or delete text in this tab |  | 1 | 1000 | Yes |  | Yes | Yes | No | No | No |  | No | No | Yes | Annually | No | No | No |  |  |  | No engagement |  | 1 | Pneumatic control | 1
| HIDE THIS TAB FROM USER |  | 2 | 1: 2000; 3: Never; 14: Seasonally | Low engagement |  | 2 | Combination DDC & Pneumatic | 3
|  |  | 3 | 1: 3000; 3: Infrequent; 14: Monthly | Some engagement |  | 3 | Web based smart thermostats | 3
|  |  | 4 | 1: 4000; 3: Regularly; 14: Weekly |  |  | 4 | Local programmable thermostats | 2
|  |  | 5 | 5000 | No | Constant | No | No | Yes | Yes | Yes |  | Yes | Yes | No | Daily | Yes | Yes | Yes |  |  |  | High engagement |  | 5 | Manual control | 2
|  |  | Weighting (relative factor, unitless - refer to graph to see order): | 90 | 50 | 30 | 80 | 20 | 70 | 10 | 10 | 60 | 40 | 20 | 70 | 30 | 20 | 20 | 35 | 100 | 100 | 100 | 50 |  |  | Other | 3
4025
| Building number |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Question | Building Name | Max
1 | Approximate floor area of conditioned space (square meters - m2) (required) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 90
2 | Is the primary space use of the building expected to significantly change in the next 5 years? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 50
3 | How often are thermal comfort or indoor air quality (IAQ) complaints received from building occupants/tenants? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 30
4 | Has the building been through a comprehensive recommissioning process where measures were implemented within the past 5 yrs? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 80
5 | Does the building currently have an Energy Performance Contract (EPC) in place? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 20
6 | Does the organization have the financial resources to implement low cost measures identified during the EBCx process at this building? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 70
7 | Do you have access to mechanical drawings for the building? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 10
8 | Do you have access to balancing reports for the building? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 10
9 | How engaged are your operators and staff with respect to building optimization? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 50
10 | What is the primary motivating factor of the organization in terms of performance improvements (for all buildings)? |  | 4025 1: 0
| Score for above statement |  | 4025 1: Not scored, but used to score various energy, cost, GHG inputs
11 | What is the primary type of building control system you have in this building? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 60
12 | If you have a digital building controls system does it have remote (off-site) access that is available for an external consultant to use? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 40
13 | Does the digital building controls system have capabilities to log and trend data? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 20
14 | Are you proceeding with a major redesign or replacement of your HVAC or control systems in the building in the near future? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 70
15 | How often do you experience premature failure of building equipment, control systems, or both in this building? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 30
16 | Are there concerns that water consumption for this building is higher than expected? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 20
17 | Are there known opportunities related to the building envelope that could improve energy performance? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 20
18 | Has energy use been trending upward without known cause? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Score for above statement | 35
MANUAL / RETSCREEN INPUT BELOW
19 | Annual energy cost ($/yr) (Total of all energy types)
Median value
| Max $/yr for score of 5 (__ x median) | 5
| Min $/yr for score of 1 (__ x median) | 0.2
$/yr score (1-5)
| Score for above statement | 0
20 | Annual Energy Use Intensity - EUI (ekWh/m2)
| Building type |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
National Avg EUI for building type (kWh/m2)
| Max EUI for score of 5 (__ x national avg) | 2
| Min EUI for score of 1 (__ x national avg) | 0.5
EUI score (1-5)
| Score for above statement | 1
21 | Annual GHG intensity - GHGi - (kg CO2e/m2)
| Province |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
National Avg GHGi for building type (kgCO2e/m2)
| Max GHGi for score of 5 (__x national avg) | 4
| Min GHGi for score of 1 (__x national avg) | 0.25
GHGi score (1-5)
| Score for above statement | 0
ESPM INPUT BELOW
22 | ENERGY STAR Score for the building (0 to 100)
| ESPM rating for score of 5 | 75
| ESPM rating for score of 1 | 25
ESPM score for tool
| Score for above statement | 1
23 | Annual Energy Cost for the building
Median value
| Max $/yr for score of 5 (__ x median) | 5
| Min $/yr for score of 1 (__ x median) | 0.2
$/yr score (1-5)
| Score for above statement | 0
24 | Total GHG Emissions Intensity for the building (kgCO2e/m2)
GHGi score (1-5)
| Score for above statement | 0
| Form of data entry selected by user |  | 4025 1: Manual entry or RETScreen
| Score to use (based on form of entry used, and organizational priority) | 100
| Vlookup column ref | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Building name
| Total score (based on questions above) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Count of scores with real values |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Max score possible with questions answered |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EBCx Score (0-10)
| Max count of scores possible | 100 1: 18
| Score penalty for each item of missing information | 100 1: 0.2
| Min number of questions required to not get penalized for missing information | 100 1: 9
| Score penalty |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
"Show stopper" factors | bar: 100 2 to 100 16
| Include in report (based on how many buildings entered in cell D12 of Facility Tab) | 16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
EBCx Readiness Score (0-10) to use in report
Rounded score (used for Statement A lookup)
[6 empty] | EUI low | 50% | of max EUI or less flags site for statement on energy performance impact being lower than other bldgs
[6 empty] | GHGi low | 50%
[6 empty] | En cost low | 50%
| LOGIC BELOW FOR TEXT THAT AUTO POPULATES IN REPORT TAB | 100 1: Ref
| The building size is small. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| The primary space use of the building expected to significantly change in the next 5 years. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| An Energy Performance Contract (EPC) is in place. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| The organization does not have the financial resources. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A major redesign of HVAC/controls is planned in the near future. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water consumption is high. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Known issues with building envelope performance | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| The building uses pnuematic controls. | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| The building has a mix of pneumatic and DDC controls. | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Low energy reduction potential in comparison to other buildings. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Low GHG reduction potential in comparison to other buildings. | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Low energy cost reduction potential in comparison to other buildings. | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Low operator engagement. | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| The building has been through EBCx within the past 5 years. | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Limited information was provided by the user in the tool. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Building name
Report statement part A
Report statement part B (only applies if score is 2 or highter, otherwise blank)
Report statement combined
Statement to the right (reasons why score is low) only shows if score for building is less than 1.5 (i.e. would round to a score of 1 or less). If low score, this text is included in the 'Report statement combined' above
Statement if limited information provided in tool
| General statements - Text to be used in report | 100 2: EBCx score; 100 3: Opening statement for report (Part A)
| THIS TEXT IN ORANGE IS THE TEXT USED TO GENERATE THE REPORT | 100 2: 10; 100 3: This building is an ideal candidate for EBCx and you should proceed with a full EBCx approach.
| THIS TEXT CAN BE EDITED AS REQUIRED. DO NOT ADD ROWS OR COLUMNS THOUGH | 100 2: 9; 100 3: This building is a strong candidate for EBCx.
|  |  | 8 | This building is a strong candidate for EBCx.
|  |  | 7 | This building is a good candidate for EBCx.
|  |  | 6 | This building is a good candidate for EBCx.
|  |  | 5 | This building is a reasonable candidate for EBCx.
|  |  | 4 | This building is a reasonable candidate for EBCx.
|  |  | 3 | This building is a low candidate for EBCx at this point in time.
|  |  | 2 | This building is a poor candidate for EBCx at this point in time.
|  |  | 1 | This building is a poor candidate for EBCx at this point in time and you should prioritize other buildings for now, but work towards addressing the reasons for this low score and reassessing this building again in the future. Reasons for a low score include:
| Condition Specific Statements - Text to be used in report | 100 2: 0; 100 3: This building is a poor candidate for EBCx at this point in time and you should prioritize other buildings for now, but work towards addressing the reasons for this low score and reassessing this building again in the future. Reasons for a low score include:
|  | Ref |  | Secondary statements for report (Part B)
| The building size is small. | 100 1: 1; 100 2: >>>>>; 100 3: This building floor area is small and the return on investment for EBCx may be low when compared to other larger buildings. Consider a light version of EBCx for this building, focusing only on primary energy consuming equipment. It is recommend to focus on other buildings that are larger where there is likely to be a greater return on the investment and effort put into EBCx.
| The primary space use of the building expected to significantly change in the next 5 years. | 100 1: 2; 100 2: >>>>>; 100 3: The proposed space use changes may have an impact on the effectiveness of the EBCx process. If these changes are planned in the next 5 years, you may wish to wait until these modifications are complete before proceeding with EBCx.
| An Energy Performance Contract (EPC) is in place. | 100 1: 3; 100 2: >>>>>; 100 3: Consider the impacts of the Energy Performance Contract (EPC) that you have in place on the ability to implement energy improvements.
| The organization does not have the financial resources. | 100 1: 4; 100 2: >>>>>; 100 3: It is recommended you first secure funding to implement low-cost measures before proceeding with EBCx.
| A major redesign of HVAC/controls is planned in the near future. | 100 1: 5; 100 2: >>>>>; 100 3: You should wait until the major HVAC and controls upgrade are completed before considering EBCx for this building. A period of at least 12 months after the upgrade is ideal as it will allow you to establish a new energy performance baseline before proceeding with the EBCx.
| Water consumption is high. | 100 1: 6; 100 2: >>>>>; 100 3: Including water consuming equipment as part of the EBCx scope will help to address concerns over excessive water usage.
| Known issues with building envelope performance | 100 1: 7; 100 2: >>>>>; 100 3: Including building envelope as part of the EBCx scope should also be considered, in particular for aspects of envelope with known issues.
| The building uses pnuematic controls. | 100 1: 8; 100 2: >>>>>; 100 3: Prior to proceeding with EBCx for this building it is recommended you prioritize upgrading the pneumatic control system to a modern control system.
| The building has a mix of pneumatic and DDC controls. | 100 1: 9; 100 2: >>>>>; 100 3: Consider focusing the EBCx on the area of the building served by the modern control system / DDC. Pneumatic controls should be prioritized for replacement.
| Low energy reduction potential in comparison to other buildings. | 100 1: 10; 100 2: >>>>>; 100 3: The energy performance impact is likely to be lower in comparison to other sites.
| Low GHG reduction potential in comparison to other buildings. | 100 1: 11; 100 2: >>>>>; 100 3: Keep in mind that the GHG impact of EBCx on this building is likely to be lower in comparison to others.
| Low energy cost reduction potential in comparison to other buildings. | 100 1: 12; 100 2: >>>>>; 100 3: The energy cost reduction is likely to be lower in comparison to other sites.
| Low operator engagement. | 100 1: 13; 100 2: >>>>>; 100 3: Increasing building operator engagement prior to starting EBCx will be critical to the success of this project.
| The building has been through EBCx within the past 5 years. | 100 1: 14; 100 2: >>>>>; 100 3: The building has been through EBCx within the past 5 years - it is recommended to prioritize other buildings that have had less recent EBCx activities.
| Limited information was provided by the user in the tool | 100 1: 15; 100 2: >>>>>; 100 3: Limited information was provided for this building in the tool. Answering more questions will increase the accuracy of the score for this building.
Ce graphique n’est pas disponible dans votre version d’Excel. La modification de cette forme ou l’enregistrement de ce classeur dans un autre format de fichier endommagera le graphique de façon irréparable.
Ce graphique n’est pas disponible dans votre version d’Excel. La modification de cette forme ou l’enregistrement de ce classeur dans un autre format de fichier endommagera le graphique de façon irréparable.
Note on X2: Sam Thomas: Added later on, reason for being on right side here.
Note on A12: Sam Thomas: For reference only, not used.
Note on B50: Sam Thomas: From 'Energy' tab
Note on C54: Sam Thomas: Column below: 1 refers to the metric the organization prioritizes (based on user input). Facility tab question 20
Note on B106: Sam Thomas: If pneumatic controls, or small building
Note on B151: Sam Thomas: All statements below need to have a space infront of them at the start to allow for spacing between sentences in report.

## EUIs (hidden)
EUIs / GHGis used to provide scoring in tool |  |  |  | Reference Code | Type | Link
|  |  |  | A | NRCan SCIEU | https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=SC&sector=aaa&juris=ca&year=2019&rn=1&page=1
|  |  |  | B | Data Ceter EUI | https://natural-resources.canada.ca/energy-efficiency/energy-star/buildings/technical-reference-documents/data-center
|  |  |  | C | ESPM EUIs | https://natural-resources.canada.ca/sites/www.nrcan.gc.ca/files/energy/pdf/Canadian%20National%20Median%20Tables-EN-Aug2018-7.pdf
|  |  |  | D | MURB EUI | https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=MURB&sector=AAA&juris=CA&rn=1&page=2
| Source | 1.42 | EUI - Other | E | ESPM GHGi | https://natural-resources.canada.ca/sites/nrcan/files/energy/pdf/2GHGI_-_English19_0(1).pdf
| Site | 0.98 | EUI - Other
| Ratio Site/Source | 69.01%
[6 empty] | Elec emission factor (kgCO2/kWh) | 0.027 | 0.26 | 0.71 | 0.26 | 0.0012 | 0.03 | 0.0012 | 0.66 | 0.62 | 0.0113 | 0.2 | 0.85 | 0.101 | From LookupTables tab
|  |  |  | x |  |  | y
|  |  |  | Site EUI |  |  | GHGi (kgCO2e/m2) - 2022 NRCan data
|  |  | Building Type | GJ/m2 | kWh/m2 | Reference/Notes | NL | PE | NS | NB | QC | ON | MB | SK | AB | BC | NT | NU | YT | Slope | I-Cept
|  |  | Banking/Financial | 0.99 | 275 | C | 22.7 | 79.9 | 165.1 | 79.9 | 12.1 | 33.2 | 28.6 | 114.5 | 109.2 | 25.9 | 57.5564 | 164.4941 | 41.2689 | 164.5195 | 24.6524
|  |  | Data Center | 14.0444 | 3901.2 | B | 105.3324 | 1014.312 | 2769.852 | 1014.312 | 4.6814 | 117.036 | 4.6814 | 2574.792 | 2418.744 | 44.0836 | 780.24 | 3316.02 | 394.0212 |  |  | For Data Centers - GHGi calculated based on EUI x elec emission factor, assuming 100% electric
|  |  | Education - K-12 | 0.75 | 208.3 | C | 17.2 | 60.5 | 125 | 60.5 | 9.2 | 25.1 | 21.6 | 86.7 | 82.7 | 19.6 | 43.575 | 124.5587 | 31.2406 | 124.5902 | 18.657
|  |  | Education - Other | 0.92 | 255.6 | C | 21.1 | 74.1 | 153.1 | 74.1 | 11.2 | 30.7 | 26.5 | 106.2 | 101.3 | 24 | 53.3674 | 152.5699 | 38.2581 | 152.6192 | 22.8436
|  |  | Education - Post Secondary | 1.01 | 280.6 | C | 23.2 | 81.6 | 168.6 | 81.6 | 12.4 | 33.8 | 29.1 | 116.9 | 111.5 | 26.4 | 58.7515 | 167.9818 | 42.1149 | 168.0465 | 25.1422
|  |  | Entertainment | 1.74 | 483.3 | C ("Education Other") | 21.5 | 75.6 | 156.3 | 75.6 | 11.5 | 31.4 | 27 | 108.4 | 103.4 | 24.5 | 54.4737 | 155.7326 | 39.0512 | 155.7829 | 23.3171
|  |  | Food - Other | 1.91 | 530.6 | C (Food Other Sales) | 43.9 | 154.6 | 319.3 | 154.6 | 23.4 | 64.1 | 55.2 | 221.5 | 211.2 | 50.1 | 111.3077 | 318.1876 | 79.7982 | 318.2769 | 47.6523
|  |  | Food - Restaurant & Bar | 3.17 | 880.6 | C | 73 | 256.9 | 530.8 | 256.9 | 38.9 | 106.6 | 91.8 | 368.2 | 351.1 | 83.3 | 185.0277 | 528.9147 | 132.651 | 529.0569 | 79.2163
|  |  | Food - Supermarket | 1.91 | 530.6 | C | 43.9 | 154.6 | 319.3 | 154.6 | 23.4 | 64.1 | 55.2 | 221.5 | 211.2 | 50.1 | 111.3077 | 318.1876 | 79.7982 | 318.2769 | 47.6523
|  |  | Health - Hospital | 2.22 | 616.7 | C | 51.1 | 179.9 | 371.7 | 179.9 | 27.3 | 74.6 | 64.3 | 257.8 | 245.9 | 58.3 | 129.5661 | 370.3798 | 92.8883 | 370.4826 | 55.4696
|  |  | Health - Other | 1.04 | 288.9 | C | 23.9 | 84.2 | 174 | 84.2 | 12.8 | 34.9 | 30.1 | 120.7 | 115.1 | 27.3 | 60.6485 | 173.383 | 43.4781 | 173.4378 | 25.9609
|  |  | Industrial - Other | 10 | 2777.8 | EUI n/a. Abritray value used. | 230.6122 | 813.2653 | 1679.5918 | 813.2653 | 123.4694 | 336.7347 | 290.8163 | 1164.2857 | 1111.2245 | 263.2653 | 585.4478 | 1673.5038 | 419.7285
|  |  | Laboratory | 0.98 | 272.2 | C | 22.6 | 79.3 | 163.9 | 79.3 | 12 | 32.9 | 28.3 | 113.7 | 108.4 | 25.7 | 57.123 | 163.315 | 40.9491 | 163.3723 | 24.4485
|  |  | Lodging - Hotel | 0.88 | 244.4 | C | 20.2 | 71.1 | 146.8 | 71.1 | 10.8 | 29.5 | 25.4 | 101.8 | 97.1 | 23 | 51.1851 | 146.2723 | 36.7025 | 146.2881 | 21.9274
|  |  | Lodging - Other | 0.88 | 244.4 | C | 20.2 | 71.1 | 146.8 | 71.1 | 10.8 | 29.5 | 25.4 | 101.8 | 97.1 | 23 | 51.1851 | 146.2723 | 36.7025 | 146.2881 | 21.9274
|  |  | Manufacturing | 10 | 2777.8 | EUI n/a. Abritray value used. | 230.6122 | 813.2653 | 1679.5918 | 813.2653 | 123.4694 | 336.7347 | 290.8163 | 1164.2857 | 1111.2245 | 263.2653 | 585.4478 | 1673.5038 | 419.7285
|  |  | Office | 0.99 | 275 | C | 22.7 | 79.9 | 165.1 | 79.9 | 12.1 | 33.2 | 28.6 | 114.5 | 109.2 | 25.9 | 57.5564 | 164.4941 | 41.2689 | 164.5195 | 24.6524
|  |  | Office/Retail Mixed | 0.98 | 272.2 | C (Mixed Use) | 22.6 | 79.3 | 163.9 | 79.3 | 12 | 32.9 | 28.3 | 113.7 | 108.4 | 25.7 | 57.123 | 163.315 | 40.9491 | 163.3723 | 24.4485
|  |  | Public - Emergency Services | 1.28 | 355.6 | C (Police Station) | 29.4 | 103.5 | 213.8 | 103.5 | 15.7 | 42.9 | 37 | 148.3 | 141.5 | 33.5 | 74.5329 | 213.0749 | 53.4319 | 213.1415 | 31.9046
|  |  | Public - Library | 1.74 | 483.3 | C | 40 | 140.8 | 290.9 | 140.8 | 21.3 | 58.4 | 50.3 | 201.8 | 192.4 | 45.6 | 101.3911 | 289.8756 | 72.6834 | 289.9763 | 43.3958
|  |  | Public - Water/Waste | 5 | 1388.9 | EUI n/a. Abritray value used. | 115.3061 | 406.6327 | 839.7959 | 406.6327 | 61.7347 | 168.3673 | 145.4082 | 582.1429 | 555.6122 | 131.6327 | 292.7239 | 836.7519 | 209.8643
|  |  | Public - Recreation | 1.51 | 419.4 | C | 34.7 | 122.2 | 252.4 | 122.2 | 18.5 | 50.7 | 43.7 | 175.1 | 167 | 39.6 | 88.0002 | 251.5334 | 63.0928 | 251.5896 | 37.6823
|  |  | Religious Worship | 0.69 | 191.7 | C | 16 | 56.2 | 116.1 | 56.2 | 8.5 | 23.3 | 20.1 | 80.5 | 76.8 | 18.2 | 40.4713 | 115.6767 | 29.0169 | 115.7006 | 17.3311
|  |  | Residential Multi Unit | 0.84 | 233.3 | D | 19.3714 | 68.3143 | 141.0857 | 68.3143 | 10.3714 | 28.2857 | 24.4286 | 97.8 | 93.3429 | 22.1143 | 49.1776 | 140.5743 | 35.2572 | 140.6103 | 21.0556
|  |  | Retail | 1.13 | 313.9 | C | 25.9 | 91.3 | 188.5 | 91.3 | 12.8 | 37.9 | 32.6 | 130.8 | 124.7 | 29.6 | 65.6097 | 187.9572 | 46.9752 | 188.227 | 27.9642
|  |  | Retail - Mall | 4.51 | 1252.8 | C | 103.8 | 365.3 | 754.8 | 365.3 | 55.4 | 151.5 | 130.5 | 523.5 | 499.3 | 118.4 | 263.0925 | 752.1031 | 188.6125 | 752.324 | 112.6277
|  |  | Retail - Other | 4.51 | 1252.8 | C | 103.8 | 365.3 | 754.8 | 365.3 | 55.4 | 151.5 | 130.5 | 523.5 | 499.3 | 118.4 | 263.0925 | 752.1031 | 188.6125 | 752.324 | 112.6277
|  |  | Retail - Store | 1.13 | 313.9 | C | 25.9 | 91.3 | 188.5 | 91.3 | 12.8 | 37.9 | 32.6 | 130.8 | 124.7 | 29.6 | 65.6097 | 187.9572 | 46.9752 | 188.227 | 27.9642
|  |  | Warehouse | 0.63 | 175 | C | 14.4 | 50.8 | 104.9 | 50.8 | 7.7 | 21.1 | 18.1 | 72.8 | 69.4 | 16.5 | 36.5773 | 104.5512 | 26.2244 | 104.5752 | 15.6623
|  |  | OTHER | 0.98 | 272.2 | C | 22.6 | 79.7 | 164.6 | 79.7 | 12.1 | 33 | 28.5 | 114.1 | 108.9 | 25.8 | 57.3739 | 164.0034 | 41.1334 | 164.0454 | 24.5648
|  |  |  | Min | 175
|  |  |  | Max | 3901.2
Note on D12: Sam Thomas: Intent is to align with ESPM building types https://www.energystar.gov/buildings/benchmark/understand_metrics/property_types

## Dev Notes (hidden)
Notes for tool owner/developer to assist with future modifications/edits to tool
HIDE TAB FROM USER
| Tool password for all VB Code/editing |  |  | 2023154 | Images below for reference…
Image 1
When editing
Do not rename existing tabs - these are referenced in VB code
To show non-public tabs used for logic, refer to Image 1 and select 'SheetVisible'.
When closing, prior to public release
In VB, for sheets that are not shown to public, select 'SheetVeryHidden' from 'Visible' drop down in properties. See image 1 to right.
For all visible sheets
In View menu, unselect all check marks. See image 3
Hide any rows or columns marked as HIDE. See image 4.
All cells that are not user inputs should be locked. (Right click on cells > Format Cells > Protection > Locked)
All cells that are user inputs should NOT be locked.
Right click on tab name, select 'Protect Sheet', use password above. See image 2,.
Image 2
Image 3
Image 4