## Introduction
K-12 School RCx Benchmarking Tool1
This energy benchmarking tool was developed to help select primary and secondary schools best suited for recommissioning. Prioritizing a building portfolio and selecting the buildings with the greatest chances of success can facilitate long-term planning and ensure a quick return on investment. This benchmarking tool was designed to be used at the planning phase of the standardized RCx process. For more information, please consult the Recommissioning (RCx) Guide for Buildings Owners and Managers, available free at the following address:
canmetenergy.nrcan.gc.ca/rcx_guide.html
Points to consider when using the benchmarking tool
The energy consumption data used must be normalized by school year (July to June) and the heating degree-days in Montreal established by Environment Canada, or 4518.7 °C-d heating degree-days (normal over 30 years 1971-2000).
The calculation methodology was established based on data from Quebec schools for the years 2004 to 2007. Using this data with schools outside Quebec or from other years is therefore an extrapolation.
To evaluate the changes in energy consumption between two years, it is important that energy consumption data be standardized and be taken from consecutive years and that the building did not change its primary heating type during those two years.
Acknowledgements
A great number of people have provided information and/or guidance during the development of this tool. The Natural Resources Canada’s CanmetENERGY would like to thank the following individuals for their assistance:
Gilles Jean, Sonia Ringuette, Alexandre Monarque, Julie Bossé and Claire Marchand of NRCan's CanmetENERGY, Philip B. Jago, Michel Lamanque and Ian Meredith of NRCan's Office of Energy Efficiency (OEE), Gilles Marchand and Hamza Benmoussa from the Ministère de l’Éducation, du Loisir et du Sport du Québec (MELS), Martin Carignan and Gina Bezeau of Statistique Différence, Daniel Bourque of Kolostat Inc., Michel Parent of Technosim, and Guy Turgeon and Annie Pageau of Therméca.
The data used in this statistical analysis was compiled and made available by the Ministère de l’Éducation, du Loisir et du Sport du Québec (MELS). The collection of the energy consumption data was made possible by the active participation of Quebec’s 69 school boards who, annually since 1977, have volunteered the information necessary to produce the energy balance of their respective building portfolios to the MELS.
As part of the various consultations conducted, numerous other organisations provided comments and suggestions for improvements. Their efforts are also gratefully acknowledged.
Main references
- Statistical Analysis of Quebec School Boards Network Energy Balance from 2004-2007, CanmetENERGY, ISBN 978-1-100-13033-0, Cat. M154-22/2009E-PDF, 2009.
- CanmetENERGY's RCx Guide for Building Owners and Managers, ISBN 978-1-100-10035-7, Cat. M39-123/2008E-PDF, NRCan, 2008.
- CanmetENERGY's Advanced RCx Course, ISBN 978-1-100-90417-7, Cat. M154-18/2008E-PDF, NRCan, Nov. 2008.
- CanmetENERGY's RETScreen International Clean Energy Project Analysis Software (Version 4), available at: www.retscreen.net.
1. See the RCx Glossary for definitions of the terminology used by Natural Resources Canada (NRCan):
canmetenergy.nrcan.gc.ca/rcx_glossary.html.
Reproduction
This tool and accompanying data are copyright of the Minister of Natural Resources Canada (2010). Duplication in any manner is forbidden without prior written permission, which may be obtained by contacting CanmetENERGY.
© Minister of Natural Resources Canada 2010.
Disclaimer & Indemnification
This tool is provided on an "as is" basis. Natural Resources Canada nor does its minister, officers, employees or agents make any representations or warranties, either expressed or implied, arising by law or otherwise, including but not limited to, implied warranties of merchantability or fitness for a particular purpose, or that the use of this tool will not infringe any intellectual property rights of third parties. In no event will Natural Resources Canada nor its minister, officers, employees or agents have any obligations or liability arising from tort, or for loss of revenue or profit, or for indirect, special, incidental or consequential damages as a result of your use of this tool.
This tool is distributed for informational purposes only and does not necessarily reflect the views of the Government of Canada nor constitute an endorsement of any commercial product or person. Neither Canada, nor its ministers, officers, employees and agents make any warranty in respect to this tool nor assume any liability arising out of this tool.
The recipient of this tool shall indemnify and save harmless Natural Resources Canada, and its employees and agents, from and against, and shall be responsible for all claims, demands, losses, costs, including solicitor and client costs, damages, actions suits or proceedings, arising out of, related to, or occasioned by any use of this tool by the recipient. Natural Resources Canada shall have the right to defend any such action or proceeding with counsel of its own selection.
NRCan/CanmetENERGY

## Benchmarking Tool - Individual
[5 empty] | m2 | 1 | [5 empty] | yes
[5 empty] | ft2 | 10.7639 | [5 empty] | no
[5 empty] | m2 | 1000
Warning! No electric consumption.
Electricity Conversion
K-12 School RCx Benchmarking Tool |  |  |  |  | kWh | 0.0036 | Warning! Total must be greater than zero.
[5 empty] | GJ | 1 | Warning! This type of heating does not have the highest consumption.
Project name |  |  |  |  | EE | 1000
Project location |  |  |  |  | EB | 0
Location of climate data | [6 empty] | Ordinary electricity |  | Information unknown |  | Information not known
[6 empty] | Natural Gaz Conversion | Dual energy electricity |  | Heating only |  | No specialized area(s)
Prepared for |  |  |  |  | m3 | 0.03789 | Natural gas |  | Heating and ventilation |  | Heavy shop(s) or cafeteria kitchen(s) only
Prepared by |  |  |  |  | kWh | 0.0036 | Oil or other(s) |  | Heating, ventilation and cooling |  | Pool(s) with or without heavy shop(s) or cafeteria kitchen(s)
[5 empty] | MBtu | 1.0551
Building characteristics and energy consumption |  |  |  |  | therm | 0.10551 | Dual energy electricity | EB | Heating and ventilation | V | Heavy shop(s) or cafeteria kitchen(s) only | 1
[5 empty] | GJ | 1 | Natural gas | G | Heating only | A | No specialized area(s) | 0
Building type |  | K-12 School |  |  |  |  | Oil or other(s) | M | Heating, ventilation and cooling | C | Pool(s) with or without heavy shop(s) or cafeteria kitchen(s) | 2
Building size | m2 | 1000 |  |  | G | 0 | Ordinary electricity | EE
Type of HVAC system |  | Information unknown |  |  |  | Mazout Conversion
Specialized area(s) |  | Information not known |  |  | m3 | 38.8 | Ordinary electricity | 650 | #VALUE! |  | Z
[5 empty] | L | 0.0388 | Dual energy electricity | 0 | 0 |  | C
[5 empty] | kWh | 0.0036 | Natural gas | 0 |  |  | 1
Data for school year analyzed |  |  |  |  | MBtu | 1.0551 | Oil or other(s) | 0
Period |  | July 2008 to June 2009 |  |  | therm | 0.10551 | Total heating | 650 | #VALUE! |  | 0
Heating-degree days (HDD) | °C-d | 4518.7 | see Environment Canada |  | GJ | 1 | PEDH | 0.65 | #VALUE! |  | 0 | 1
Break down the energy consumption? |  | no |  |  | M | 0 | max value | 650 | #VALUE! |  | 1 | 0 | 1
Ordinary electricity | GJ | 1000 |  |  |  |  | Heating type | Ordinary electricity | #VALUE! |  | 0
Dual energy electricity | GJ | 0 |  |  | T1 | 1000
Natural gas | GJ | 0 |  |  | T2 | 1000 |  | HDD reference (Montreal, QC) | 4518.7 |  | Building type
Oil or other(s) | GJ | 0
Total energy consumption | GJ | 1000 | [8 empty] | 0 | Building with low energy consumption
Total energy consumption | GJ | 1000 |  |  |  | Stable | 3 |  | Comparable | 3 | 6 | Building with ordinary energy consumption
Primary heating defined by the user? |  | yes |  |  |  | Strong decrease | 2 |  | High | 4 | 12 | Good RCx candidate
Primary heating source |  | Ordinary electricity |  |  |  | Strong increase | 4 |  | Low | 2 | 20 | Very good RCx candidate
|  | Ordinary electricity |  |  |  | Very strong decrease | 1 |  | Very high | 5 | 25 | Excellent RCx candidate
Proportion of energy dedicated to heating |  | 65% |  |  |  | Very strong increase | 5 |  | Very low | 1 | 25 | max
Standardized energy consumption | GJ | 1000
Energy Use index (EUI) | GJ/m² | 1 | [5 empty] | résultats
[7 empty] | Based on total energy consumption | 3 | 1 |  | 100%
Enter data for the previous year? |  | no |  |  |  |  | Specific to the building type | 2 | 0 | 1 | 100% | Unknown, data missing
[7 empty] | Based on variation of previous school year | 3 | 0 | 0 | 100%
Data for the previous school year | [8 empty] | 1 | 0
Period |  | July 2007 to june 2008
Heating-degree days (HDD) | °C-d | 4518.7 | see Environment Canada |  |  |  |  | 1 | 2 | 3 | 4 | 5
Total energy consumption | GJ | 1000 |  |  | 0 | 1 |  | Très bas | Bas | Comparable | Élevé | Très élevé
Proportion of energy dedicated to heating |  | 65% |  |  | 1 | 1 | Very strong decrease | 0 | 0 | 0 | 6 | 12
Standardized energy consumption | GJ | 1000 |  |  | 2 | 2 | Strong decrease | 0 | 0 | 0 | 6 | 12
Energy Use index (EUI) | GJ/m² | 1 |  |  | 3 | 3 | Stable | 0 | 0 | 6 | 12 | 20
Variation with the year analysed | % | 0% |  |  | 4 | 4 | Strong increase | 6 | 6 | 12 | 12 | 20
[5 empty] | 5 | 5 | Very strong increase | 12 | 12 | 20 | 20 | 25
Building RCx potential by energy benchmarking |  | Result | [5 empty] | Axis1 (GJ) | Axis2 (delta) | Axis1 (GJ) | Axis2 (delta)
[6 empty] | Axis1 (GJ) | Axis2 (delta) | 100% | 0% | position | position | result | Potential
Based on total energy consumption |  | Comparable |  |  |  | 3 | 0 | 3 | 0 | 3 | 1 | 0 | Building with low energy consumption
Specific to the building type |  | Unknown, data missing
Based on variation of previous school year |  | Stable |  |  |  | Based on total consumption | 1
[6 empty] | c20-c21 | 0
Combined potential |  | Building with low energy consumption |  |  |  | c36 | 1
[6 empty] | Based on building type | 0
[6 empty] | variation over 2 years | FALSE
© Natural Resources Canada 2010. |  |  |  | NRCan/CanmetENERGY

## Benchmarking Tool - Multiple
| Électrique | EE |  | Chauffage seulement | C | [6 empty] | Aucune | 0
| Électrique biénergie | EB |  | Avec ventilation | V | [6 empty] | Atelier lourd seulement | 1
| Gaz naturel | G |  | Avec climatisation | A | [6 empty] | Atelier lourd et piscine | 2
| Mazout et autres | M
# | Type de Chauffage principal |  |  | # | Type de CVAC | [6 empty] | # | Type de Zone(s) spécialisée(s)
0 | EE = Électrique |  |  | 0 | C = Chauffage seulement | [6 empty] | 0 | 0 = Aucune
4 | EB = Électrique biénergie |  |  | 3 | V = Avec ventilation | [6 empty] | 0 | 1 = Atelier lourd seulement
0 | G = Gaz naturel |  |  | 1 | A = Avec climatisation | [6 empty] | 0 | 2 = Atelier lourd et piscine
0 | M = Mazout et autres
K-12 School RCx Benchmarking Tool
Résumé des données d'étalonnages multiples entrées |  |  |  | Consommation | Année analysée | Année précédente
7 | données pour le calcul de la consommation énergétique |  |  | Valeur maximale | 1.2 | 1.32 | [5 empty] | GJ/m2 |  |  |  | donnée | données | pour le calcul de la consommation énergétique
7 | données pour le calcul spécifique au type de bâtiment |  |  | Valeur minimale | 0.4 | 0.11 | [5 empty] | GJ/m2 |  |  |  | donnée | données | pour le calcul spécifique au type de bâtiment
7 | données pour le calcul de la variation avec l'année précédente |  |  | Valeur moyenne | 1.0286 | 0.73857 | [5 empty] | GJ/m2 |  |  |  | donnée | données | pour le calcul de la variation avec l'année précédente
7 | résultats pour le calcul du potentiel combiné |  |  | Écart-type | 0.28702 | 0.5349 | [5 empty] | GJ/m2 |  |  |  | résultat | résultats | pour le calcul du potentiel combiné
[16 empty] | validation column L | validation column M | validation column N | validation column O | selon la consommation énergétique totale | spécifique au type de bâtiments | selon la variation avec l'année scolaire précédente | test pour considérer ou non L | test pour considérer ou non M | test pour considérer ou non N | sum L, M, N | test2 pour savoir L ou M | test2 pour savoir N | sum2 (L ou M) vs N | Axe1 (GJ) | Axe2 (delta) | Axe1 (GJ) normalisée | Axe2 (delta) normalisée | Axe1 (GJ) POSITION | Axe2 (delta) POSITION | Résultat
Code | Name | Region | Size | Standardized consumption for the school year analyzed | Standardized consumption for the previous school year | Building Type (see worksheet 'Help' for definitions) | Source de chauffage principale | Type de CVAC | Type de Zone(s) spécialisée(s) | vérification | différence entre les deux années | RCx potential based on energy consumption | RCx potential based on the building type | RCx potential based on variation with the previous year | Combined RCx potential | [23 empty] | 100% | 100% | 100%
|  |  | m2 | GJ/m2 | GJ/m2
A1 | School #1 | Region #1 | 100000 | 1 | 0.81 | EBA2 | EB | A | 2 | 4 | 0.23457 | Comparable | Comparable | Strong increase | Good | OK | OK | OK | OK | 3 | 3 | 4 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 4 | 3 | 4 | 3 | 4 | 12 | EBA0 | [6 empty] | 0 | Poor
A2 | School #2 | Region #1 | 10000 | 1.1 | 0.11 | EBV1 | EB | V | 1 | 12 | 9 | Comparable | High | Very strong increase | Very good | OK | OK | OK | OK | 3 | 4 | 5 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 4 | 5 | 4 | 5 | 20 | EBA1 |  | Stable | 3 |  | Comparable | 3 | 6 | Regular
A3 | School #3 | Region #1 | 1000 | 1.2 | 1.32 | EEC0 | E | E | 0 | 12 | -0.090909 | High | Comparable | Stable | Regular | OK | OK | OK | OK | 4 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | EBA2 |  | Strong decrease | 2 |  | High | 4 | 12 | Good
A4 | School #4 | Region #1 | 100 | 1.2 | 1.1 | EBV1 | EB | V | 1 | 12 | 0.090909 | High | High | Stable | Good | OK | OK | OK | OK | 4 | 4 | 3 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 4 | 3 | 4 | 3 | 4 | 3 | 12 | EBC0 |  | Strong increase | 4 |  | Low | 2 | 20 | Very good
B1 | School #1 | Region #2 | 100000 | 0.4 | 0.4 | EEA2 | E | E | 2 | 12 | 0 | Comparable | Comparable | Stable | Regular | OK | OK | OK | OK | 3 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | EBC1 |  | Very strong decrease | 1 |  | Very high | 5 | 25 | Excellent
B2 | School #2 | Region #2 | 10000 | 1.1 | 0.11 | EBV1 | EB | V | 1 | 12 | 9 | Comparable | High | Very strong increase | Very good | OK | OK | OK | OK | 3 | 4 | 5 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 4 | 5 | 4 | 5 | 4 | 5 | 20 | EBC2 |  | Very strong increase | 5 |  | Very low | 1 | 25 | Excellent
B3 | School #3 | Region #2 | 1000 | 1.2 | 1.32 | EEC0 | E | E | 0 | 12 | -0.090909 | High | Comparable | Stable | Regular | OK | OK | OK | OK | 4 | 3 | 3 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | EBV0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EBV1 |  |  |  | 1 | 2 | 3 | 4 | 5
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EBV2 |  |  |  | Very low | Low | Comparable | High | Very high
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEA0 |  | 1 | Very strong decrease | 0 | 0 | 0 | 6 | 12
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEA1 |  | 2 | Strong decrease | 0 | 0 | 0 | 6 | 12
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEA2 |  | 3 | Stable | 0 | 0 | 6 | 12 | 20
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEC0 |  | 4 | Strong increase | 6 | 6 | 12 | 12 | 20
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEC1 |  | 5 | Very strong increase | 12 | 12 | 20 | 20 | 25
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEC2
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEV0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEV1
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | EEV2
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GA0 | A |  | Missing data
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GA1 | B | 0 | No consumption
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GA2
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GC0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GC1 |  |  |  | standardized value | Position
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GC2 |  |  |  | 0 | 1
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GV0 |  |  |  | 1 | 1
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GV1 |  |  |  | 1.5 | 2
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | GV2 |  |  |  | 2 | 2
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MA0 |  |  |  | 2.5 | 3
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MA1 |  |  |  | 3 | 3
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MA2 |  |  |  | 3.5 | 4
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MC0 |  |  |  | 4 | 4
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MC1 |  |  |  | 4.5 | 5
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MC2 |  |  |  | 5 | 5
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MV0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MV1
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | MV2
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0
[10 empty] | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0
© Ministre de Ressources naturelles Canada 2010. | [14 empty] | RNCan/CanmetÉNERGIE

## Help
K-12 School RCx Benchmarking Tool
Input and Output Cell Colour Coding
The user enters data into coloured worksheet cells. All other cells that do not require input data are protected to prevent the user from mistakenly deleting a formula or reference cell. The tool cell colour coding chart shows the colour coding for input and output cells.
Output data - calculated by the model.
User input data - required by the model.
User input data - for reference purposes only (not required by the model).
Source : RETScreen International Clean Energy Project Analysis Software Cell Colour Coding.
Alphanumeric code to define the type of building for the multiple benchmarking tool
Buildings must be classified according to the primary heating source, the presence of mechanical ventilation systems and the presence of specialized areas. They are classified using an alphanumeric code of three variables listed in the table below. Note that a "heavy shop" is a room with local air exhaust of at least 2,000 litres/second.
Example: A building primarily heated by natural gas, with a cooling system but no pool, heavy shop or cafeteria kitchen, receives these three alphanumeric characters: GC0.
| Variable | Alphanumeric character
| Primary heating source | EE: Electricity with ordinary rates is the primary heating source.
EB: Electricity with dual energy rates is the primary heating source.
G: Natural gas is the primary heating source.
M: Oil is the primary heating source.
| Presence of ventilation or cooling | A: Most of the building is neither ventilated nor cooled (i.e. heating only).
V: Most of the building is ventilated mechanically.
C: Most of the building is cooled mechanically.
-- : Information inconnue
| Presence of a specialized area | 0: No specialized area
1: Heavy shop(s) and/or cafeteria kitchen(s) only (no pool).
2: Pool(s) with or without heavy shop(s) or cafeteria kitchen(s).
-- : Information inconnue
Source: Ministère de l’Éducation, du Loisir et du Sport du Québec (MELS). "Guide explicatif – Relevé de la consommation énergétique 2006-2007", October 2007.
© Natural Resources Canada 2010. |  |  | NRCan/CanmetENERGY

## Tableaux calculsE (hidden)
Année | [6 empty] | Constante 1 | Constante 2 | Constante 3 | Constante 4 |  | Année comparaison | [5 empty] | Constante 1 | Constante 2 | Constante 3 | Constante 4 | [7 empty] | Constante 1 | Constante 2 | Constante 3 | Constante 4
20006-2007 | [6 empty] | 3 | 1.5 | 3 | 1.5 |  | 2005-2006 | [5 empty] | 3 | 1.5 | 3 | 1.5 | [7 empty] | 3 | 1.5 | 3 | 1.5
| Consommation énergétique | [5 empty] | Élevée |  | Basse |  |  | Différence | [5 empty] | Élevée |  | Basse |  |  | Global | [5 empty] | Élevée |  | Basse
Types de bâtiments | Année de référence | N | Médiane | Rang interquartile | 25% | 75% | Limite 1 | Limite 2 | Limite 3 | Limite 4 | Consommation | Année précédente | N | Médiane | Rang interquartile | 25% | 75% | Limite 1 | Limite 2 | Limite 3 | Limite 4 | Tendance | Année de référence | N | Médiane | Rang interquartile | 25% | 75% | Limite 1 | Limite 2 | Limite 3 | Limite 4
EBA0 | 2005-2006 | 575 | 0.47827 | 0.14779 | 0.41254 | 0.56034 | 1.0037 | 0.78203 | 0 | 0.19086 | Very low | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% | Very strong decrease | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EBA1 | 2005-2006 | 28 | 0.46723 | 0.22862 | 0.38164 | 0.61027 | 1.2961 | 0.9532 | 0 | 0.038711 | Low | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% | Strong decrease | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EBA2 | 2005-2006 | 17 | 0.74097 | 0.24484 | 0.60499 | 0.84984 | 1.5844 | 1.2171 | 0 | 0.23773 | Comparable | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% | Stable | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EBC0 | 2005-2006 | 21 | 0.6034 | 0.15439 | 0.53493 | 0.68932 | 1.1525 | 0.9209 | 0.071763 | 0.30334 | High | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% | Strong increase | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EBC1 | 2005-2006 | 21 | 0.6034 | 0.15439 | 0.53493 | 0.68932 | 1.1525 | 0.9209 | 0.071763 | 0.30334 | Very high | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% | Very strong increase | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EBC2 | 2005-2006 | 17 | 0.74097 | 0.24484 | 0.60499 | 0.84984 | 1.5844 | 1.2171 | 0 | 0.23773 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EBV0 | 2005-2006 | 78 | 0.54213 | 0.1483 | 0.47027 | 0.61857 | 1.0635 | 0.84103 | 0.025358 | 0.24781 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EBV1 | 2005-2006 | 30 | 0.62285 | 0.24426 | 0.48914 | 0.73341 | 1.4662 | 1.0998 | 0 | 0.12275 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EBV2 | 2005-2006 | 17 | 0.74097 | 0.24484 | 0.60499 | 0.84984 | 1.5844 | 1.2171 | 0 | 0.23773 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEA0 | 2006-2007 | 243 | 0.46399 | 0.13986 | 0.3926 | 0.53246 | 0.95204 | 0.74225 | 0 | 0.18282 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEA1 | 2006-2007 | 28 | 0.46723 | 0.22862 | 0.38164 | 0.61027 | 1.2961 | 0.9532 | 0 | 0.038711 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEA2 | 2005-2006 | 17 | 0.74097 | 0.24484 | 0.60499 | 0.84984 | 1.5844 | 1.2171 | 0 | 0.23773 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEC0 | 2006-2007 | 13 | 0.65667 | 0.48996 | 0.42171 | 0.91167 | 2.3815 | 1.6466 | 0 | 0 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEC1 | 2005-2006 | 21 | 0.6034 | 0.15439 | 0.53493 | 0.68932 | 1.1525 | 0.9209 | 0.071763 | 0.30334 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEC2 | 2005-2006 | 17 | 0.74097 | 0.24484 | 0.60499 | 0.84984 | 1.5844 | 1.2171 | 0 | 0.23773 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEV0 | 2006-2007 | 147 | 0.48336 | 0.13485 | 0.41696 | 0.55181 | 0.95636 | 0.75408 | 0.012406 | 0.21468 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEV1 | 2006-2007 | 22 | 0.5684 | 0.3308 | 0.38568 | 0.71648 | 1.7089 | 1.2127 | 0 | 0 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
EEV2 | 2005-2006 | 17 | 0.74097 | 0.24484 | 0.60499 | 0.84984 | 1.5844 | 1.2171 | 0 | 0.23773 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GA0 | 2006-2007 | 803 | 0.68679 | 0.2466 | 0.58078 | 0.82739 | 1.5672 | 1.1973 | 0 | 0.21088 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GA1 | 2006-2007 | 31 | 0.70682 | 0.29262 | 0.61707 | 0.9097 | 1.7876 | 1.3486 | 0 | 0.17814 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GA2 | 2006-2007 | 25 | 0.88739 | 0.44308 | 0.73719 | 1.1803 | 2.5095 | 1.8449 | 0 | 0.072567 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GC0 | 2006-2007 | 27 | 0.73138 | 0.20961 | 0.65174 | 0.86136 | 1.4902 | 1.1758 | 0.02291 | 0.33733 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GC1 | 2006-2007 | 49 | 0.91379 | 0.45362 | 0.73805 | 1.1917 | 2.5525 | 1.8721 | 0 | 0.057619 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GC2 | 2006-2007 | 35 | 0.98631 | 0.36732 | 0.83494 | 1.2023 | 2.3042 | 1.7532 | 0 | 0.28396 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GV0 | 2006-2007 | 247 | 0.73788 | 0.24193 | 0.64584 | 0.88777 | 1.6136 | 1.2507 | 0 | 0.28294 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GV1 | 2006-2007 | 93 | 0.79083 | 0.28099 | 0.69272 | 0.97371 | 1.8167 | 1.3952 | 0 | 0.27123 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
GV2 | 2006-2007 | 25 | 0.88739 | 0.44308 | 0.73719 | 1.1803 | 2.5095 | 1.8449 | 0 | 0.072567 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MA0 | 2006-2007 | 557 | 0.57758 | 0.18278 | 0.48628 | 0.66906 | 1.2174 | 0.94323 | 0 | 0.2121 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MA1 | 2006-2007 | 22 | 0.53482 | 0.21979 | 0.45719 | 0.67698 | 1.3363 | 1.0067 | 0 | 0.12751 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MA2 | 2006-2007 | 23 | 0.67101 | 0.20472 | 0.56441 | 0.76913 | 1.3833 | 1.0762 | 0 | 0.25734 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MC0 | 2006-2007 | 119 | 0.66569 | 0.19441 | 0.57853 | 0.77295 | 1.3562 | 1.0646 | 0 | 0.28691 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MC1 | 2006-2007 | 23 | 0.67101 | 0.20472 | 0.56441 | 0.76913 | 1.3833 | 1.0762 | 0 | 0.25734 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MC2 | 2006-2007 | 23 | 0.67101 | 0.20472 | 0.56441 | 0.76913 | 1.3833 | 1.0762 | 0 | 0.25734 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MV0 | 2006-2007 | 119 | 0.66569 | 0.19441 | 0.57853 | 0.77295 | 1.3562 | 1.0646 | 0 | 0.28691 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MV1 | 2006-2007 | 23 | 0.67101 | 0.20472 | 0.56441 | 0.76913 | 1.3833 | 1.0762 | 0 | 0.25734 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
MV2 | 2006-2007 | 23 | 0.67101 | 0.20472 | 0.56441 | 0.76913 | 1.3833 | 1.0762 | 0 | 0.25734 |  | 2005-2006 | 1876 | -2.41% | 10.18% | -7.52% | 2.66% | 33.2% | 17.93% | -38.06% | -22.79% |  | 2006-2007 | 2527 | 0.6364 | 0.2679 | 0.51813 | 0.78598 | 1.5897 | 1.1878 | 0 | 0.11628
Note on A8: Référence EXX2
Note on A9: Référence EXX
Note on A10: Référence EXX
Note on A11: Référence EXX2
Note on A14: Référence EEX2
Note on A16: Référence EBA1
Note on A17: Référence EXX2
Note on A19: Référence EXX
Note on A20: Référence EXX2
Note on A23: Référence EXX2
Note on A26: Référence GV2
Note on A35: Référence MV1
Note on A36: Référence MV0
Note on A37: Référence MV1
Note on A38: Référence MV1
Note on A41: Référence MV1